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	Date:
	July 15, 2026
	

	To:
	Plan Holders
	Re:
	Harper College: Bldg M Pool Pit HVAC Modifications

	Cc:
	Steve Petersen
	Cc:
	Harper Purchasing



This Addendum forms a part of the Bidding Documents and amends the original documents dated June 30, 2026.
Acknowledge receipt of this addendum in the space provided on Bid Form. Failure to do so may subject bidder to disqualification.

CONTRACTOR QUESTIONS
1. What type of controller is on terminal unit VAV-0.26?
a. Distech ECB-VAV BACnet
2. Does the existing controller located in the pit area have sufficient spare I/O to accommodate the new water detectors?
a. Yes. The controller has (2) space inputs. Only one is required for the water detectors as they can be wired in series.
3. Where is the control panel out of which the new Building B visual alarms for water and gas alarms located?
a. The control panel to which the existing steam alarm strobe is wired is located approximately 20 feet east of the strobe locations on the north wall of the boiler room.
b. We have confirmed that this panel includes (2) Distech controllers with spare output points to control the new strobes.
4. Please confirm the work hours for work inside the locker room.
c. Work within the men’s locker room must be performed off hours, i.e. between 9 pm and 6 am. All other work can be performed during normal hours.
5. What controllers are allowed?
d. No new controllers are required by project scope.
6. Who is to provide the integration and graphics updates to the campus supervisory system?
e. Integration of the new control points into the campus Tridium system shall be performed by Fixx Consulting, the campus integration provider. Contact Dan Lewand, 847.296.4000.
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